## Ventilation
Pressure (enter new value) | 1000 | hPa | (Air pressure at sea level is 1000 hPa)
| egg store | setter room | incubator | Units
Conditions (enter new values)
Temperature | 20 | 25 | 37 | ºC
Humidity | 80 | 50 | 55 | %
Calculations (results)
Moisture content (Xh) | 11.9117 | 10.1728 | 22.9175 | g/kg
Dew point (Td) | 16.4443 | 13.8563 | 26.4574 | ºC
Energy content (h) | 50.4294 | 51.1628 | 96.2663 | kJ/kg dry air
Abs moisture content | 13.8243 | 11.5096 | 24.125 | g/m3
Condensation? |  | no | yes
Incubator settings (enter new values)
Capacity | 57600 | eggs
RQ | 0.67
Fertility | 100 | %
Egg weight | 60 | g
Egg weight loss | 11 | %
Extra spray | 0 | l/hr
| Air in | Air out
T-air | 25 | 37 | ºC
RH-air | 50 | 55 | %
Energy content | 51.1628 | 96.2663 | kJ/kg dry air
CO2 | 300 | 4000 | ppm
O2 | 20 | 19 | %
day | HP (W/egg) | CO2 (L/hr) | O2 (L/hr) | H2O (kg/hr) | Heat (MJ) | V-CO2 | V-O2 | V-H2O | V-heat
1 | 0 | 0 | 0 | 0.88 | 0 | 0 | 0 | 69.7565 | 0
2 | 0.002 | 14.2129 | 21.2133 | 0.88 | 0.49766 | 3.8413 | 2.1213 | 69.7565 | 11.0338
3 | 0.0035 | 24.8726 | 37.1233 | 0.88 | 0.87091 | 6.7223 | 3.7123 | 69.7565 | 19.3092
4 | 0.006 | 42.6387 | 63.6399 | 0.88 | 1.493 | 11.524 | 6.364 | 69.7565 | 33.1015
5 | 0.0075 | 53.2984 | 79.5499 | 0.88 | 1.8662 | 14.405 | 7.955 | 69.7565 | 41.3769
6 | 0.0095 | 67.5113 | 100.7632 | 0.88 | 2.3639 | 18.2463 | 10.0763 | 69.7565 | 52.4107
7 | 0.012 | 85.2775 | 127.2798 | 0.88 | 2.986 | 23.048 | 12.728 | 69.7565 | 66.203
8 | 0.015 | 106.5968 | 159.0997 | 0.88 | 3.7325 | 28.81 | 15.91 | 69.7565 | 82.7537
9 | 0.02 | 142.1291 | 212.133 | 0.88 | 4.9766 | 38.4133 | 21.2133 | 69.7565 | 110.3383
10 | 0.032 | 227.4066 | 339.4128 | 0.88 | 7.9626 | 61.4612 | 33.9413 | 69.7565 | 176.5412
11 | 0.044 | 312.684 | 466.6926 | 0.88 | 10.9486 | 84.5092 | 46.6693 | 69.7565 | 242.7442
12 | 0.065 | 461.9196 | 689.4322 | 0.88 | 16.1741 | 124.8431 | 68.9432 | 69.7565 | 358.5994
13 | 0.095 | 675.1132 | 1007.6317 | 0.88 | 23.639 | 182.463 | 100.7632 | 69.7565 | 524.1068
14 | 0.113 | 803.0294 | 1198.5514 | 0.88 | 28.118 | 217.035 | 119.8551 | 69.7565 | 623.4112
15 | 0.132 | 938.0521 | 1400.0777 | 0.88 | 32.8458 | 253.5276 | 140.0078 | 69.7565 | 728.2326
16 | 0.14 | 994.9037 | 1484.9309 | 0.88 | 34.8365 | 268.8929 | 148.4931 | 69.7565 | 772.3679
17 | 0.145 | 1030.436 | 1537.9642 | 0.88 | 36.0806 | 278.4962 | 153.7964 | 69.7565 | 799.9525
18 | 0.15 | 1065.9683 | 1590.9974 | 0.88 | 37.3248 | 288.0995 | 159.0997 | 69.7565 | 827.537
Specific heat of eggs: |  | 3.4 | kJ per ºC per kg
Specific heat of air: |  | 1 | kJ per ºC per kg
Evaporative heat loss: |  | 2260 | kJ per liter of water
To decrease ET with 1oC |  | 11750.4 | kJ
To cool eggs down 1oC |  | 5.1993 | l of water
Moisture loss eggs |  | 0.88 | l/hr | cools down eggs with |  | 0.16925 | ºC
Extra spray |  | 0 | l/hr | cools down eggs with |  | 0 | ºC
[5 empty] | Total | 0.16925 | ºC
day
Ventilation rate at day | 18 | 288.0995 | m3/hr
Required moisture for balance |  | 12.6153 | g/m3, or | 3.6345 | l/hr
Increase in moisture content by egg weight loss |  | 3.0545 | g/m3, or | 0.88 | l/hr
Spray required for balance |  | 9.5608 | g/m3, or | 2.7545 | l/hr

## data
| Constants |  |  | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 20 | 25 | 37
A | 6.1164 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
m | 7.5914 | - | 5 | 0.53952 | 0.57589 | 0.61445 | 0.65532 | 0.69862 | 0.74448 | 0.79304 | 0.84444 | 0.89884 | 0.9564 | 1.0173 | 1.0817 | 1.1498 | 1.2217 | 1.2978 | 1.3782 | 1.4631 | 1.5529 | 1.6477 | 1.7479 | 1.8536 | 1.9654 | 2.0834 | 2.2081 | 2.3397 | 2.4788
Tn | 240.7263 | - | 10 | 1.079 | 1.1518 | 1.2289 | 1.3106 | 1.3972 | 1.489 | 1.5861 | 1.6889 | 1.7977 | 1.9128 | 2.0346 | 2.1633 | 2.2995 | 2.4434 | 2.5956 | 2.7564 | 2.9263 | 3.1058 | 3.2954 | 3.4957 | 3.7073 | 3.9308 | 4.1668 | 4.4161 | 4.6794 | 4.9575
B | 621.9907 | g/kg | 15 | 1.6186 | 1.7277 | 1.8434 | 1.966 | 2.0959 | 2.2334 | 2.3791 | 2.5333 | 2.6965 | 2.8692 | 3.0519 | 3.245 | 3.4493 | 3.6652 | 3.8934 | 4.1346 | 4.3894 | 4.6587 | 4.9431 | 5.2436 | 5.5609 | 5.8962 | 6.2502 | 6.6242 | 7.0191 | 7.4363
|  |  | 20 | 2.1581 | 2.3036 | 2.4578 | 2.6213 | 2.7945 | 2.9779 | 3.1722 | 3.3778 | 3.5954 | 3.8256 | 4.0691 | 4.3267 | 4.599 | 4.8869 | 5.1912 | 5.5128 | 5.8525 | 6.2116 | 6.5908 | 6.9914 | 7.4146 | 7.8616 | 8.3336 | 8.8322 | 9.3588 | 9.9151
|  |  | 25 | 2.6976 | 2.8795 | 3.0723 | 3.2766 | 3.4931 | 3.7224 | 3.9652 | 4.2222 | 4.4942 | 4.782 | 5.0864 | 5.4084 | 5.7488 | 6.1086 | 6.489 | 6.8909 | 7.3157 | 7.7644 | 8.2385 | 8.7393 | 9.2682 | 9.8269 | 10.417 | 11.0403 | 11.6985 | 12.3938
|  |  | 30 | 3.2371 | 3.4553 | 3.6867 | 3.9319 | 4.1917 | 4.4669 | 4.7582 | 5.0667 | 5.3931 | 5.7384 | 6.1037 | 6.49 | 6.8985 | 7.3303 | 7.7868 | 8.2691 | 8.7788 | 9.3173 | 9.8862 | 10.4871 | 11.1219 | 11.7923 | 12.5004 | 13.2483 | 14.0382 | 14.8726
|  |  | 35 | 3.7766 | 4.0312 | 4.3012 | 4.5872 | 4.8903 | 5.2114 | 5.5513 | 5.9111 | 6.2919 | 6.6948 | 7.121 | 7.5717 | 8.0483 | 8.5521 | 9.0846 | 9.6473 | 10.242 | 10.8702 | 11.5339 | 12.235 | 12.9755 | 13.7577 | 14.5838 | 15.4564 | 16.3779 | 17.3514
|  |  | 40 | 4.3161 | 4.6071 | 4.9156 | 5.2426 | 5.589 | 5.9558 | 6.3443 | 6.7555 | 7.1907 | 7.6512 | 8.1383 | 8.6534 | 9.198 | 9.7738 | 10.3824 | 11.0255 | 11.7051 | 12.4231 | 13.1816 | 13.9829 | 14.8292 | 15.7231 | 16.6672 | 17.6644 | 18.7177 | 19.8301
|  |  | 45 | 4.8557 | 5.183 | 5.5301 | 5.8979 | 6.2876 | 6.7003 | 7.1374 | 7.6 | 8.0896 | 8.6076 | 9.1556 | 9.7351 | 10.3478 | 10.9955 | 11.6802 | 12.4037 | 13.1682 | 13.976 | 14.8293 | 15.7307 | 16.6828 | 17.6885 | 18.7506 | 19.8725 | 21.0574 | 22.3089
|  |  | 50 | 5.3952 | 5.7589 | 6.1445 | 6.5532 | 6.9862 | 7.4448 | 7.9304 | 8.4444 | 8.9884 | 9.564 | 10.1728 | 10.8167 | 11.4975 | 12.2172 | 12.978 | 13.7819 | 14.6314 | 15.5289 | 16.477 | 17.4786 | 18.5365 | 19.6539 | 20.834 | 22.0805 | 23.3971 | 24.7877
|  |  | 55 | 5.9347 | 6.3348 | 6.759 | 7.2085 | 7.6848 | 8.1893 | 8.7234 | 9.2889 | 9.8873 | 10.5204 | 11.1901 | 11.8984 | 12.6473 | 13.439 | 14.2758 | 15.1601 | 16.0945 | 17.0818 | 18.1247 | 19.2264 | 20.3901 | 21.6193 | 22.9175 | 24.2886 | 25.7368 | 27.2664
|  |  | 60 | 6.4742 | 6.9107 | 7.3734 | 7.8638 | 8.3834 | 8.9338 | 9.5165 | 10.1333 | 10.7861 | 11.4768 | 12.2074 | 12.9801 | 13.797 | 14.6607 | 15.5736 | 16.5383 | 17.5576 | 18.6347 | 19.7724 | 20.9743 | 22.2438 | 23.5847 | 25.0009 | 26.4966 | 28.0765 | 29.7452
|  |  | 65 | 7.0137 | 7.4866 | 7.9879 | 8.5192 | 9.082 | 9.6782 | 10.3095 | 10.9778 | 11.685 | 12.4332 | 13.2247 | 14.0617 | 14.9468 | 15.8824 | 16.8714 | 17.9165 | 19.0208 | 20.1875 | 21.4201 | 22.7222 | 24.0974 | 25.55 | 27.0843 | 28.7047 | 30.4162 | 32.2239
|  |  | 70 | 7.5533 | 8.0625 | 8.6023 | 9.1745 | 9.7807 | 10.4227 | 11.1025 | 11.8222 | 12.5838 | 13.3896 | 14.242 | 15.1434 | 16.0965 | 17.1041 | 18.1691 | 19.2946 | 20.4839 | 21.7404 | 23.0678 | 24.47 | 25.9511 | 27.5154 | 29.1677 | 30.9127 | 32.7559 | 34.7027
|  |  | 75 | 8.0928 | 8.6384 | 9.2168 | 9.8298 | 10.4793 | 11.1672 | 11.8956 | 12.6666 | 13.4826 | 14.346 | 15.2593 | 16.2251 | 17.2463 | 18.3259 | 19.4669 | 20.6728 | 21.9471 | 23.2933 | 24.7155 | 26.2179 | 27.8047 | 29.4808 | 31.2511 | 33.1208 | 35.0956 | 37.1815
|  |  | 80 | 8.6323 | 9.2143 | 9.8312 | 10.4851 | 11.1779 | 11.9117 | 12.6886 | 13.5111 | 14.3815 | 15.3024 | 16.2765 | 17.3068 | 18.3961 | 19.5476 | 20.7647 | 22.051 | 23.4102 | 24.8462 | 26.3632 | 27.9657 | 29.6584 | 31.4462 | 33.3345 | 35.3288 | 37.4353 | 39.6602
|  |  | 85 | 9.1718 | 9.7902 | 10.4457 | 11.1404 | 11.8765 | 12.6561 | 13.4817 | 14.3555 | 15.2803 | 16.2588 | 17.2938 | 18.3884 | 19.5458 | 20.7693 | 22.0625 | 23.4292 | 24.8733 | 26.3991 | 28.0109 | 29.7136 | 31.512 | 33.4116 | 35.4179 | 37.5369 | 39.775 | 42.139
|  |  | 90 | 9.7113 | 10.366 | 11.0601 | 11.7958 | 12.5751 | 13.4006 | 14.2747 | 15.2 | 16.1792 | 17.2152 | 18.3111 | 19.4701 | 20.6956 | 21.991 | 23.3603 | 24.8074 | 26.3365 | 27.952 | 29.6586 | 31.4614 | 33.3657 | 35.377 | 37.5013 | 39.745 | 42.1147 | 44.6178
|  |  | 95 | 10.2508 | 10.9419 | 11.6746 | 12.4511 | 13.2738 | 14.1451 | 15.0677 | 16.0444 | 17.078 | 18.1716 | 19.3284 | 20.5518 | 21.8453 | 23.2128 | 24.6581 | 26.1856 | 27.7996 | 29.5049 | 31.3063 | 33.2093 | 35.2193 | 37.3424 | 39.5847 | 41.953 | 44.4544 | 47.0965
|  |  | 100 | 10.7904 | 11.5178 | 12.2891 | 13.1064 | 13.9724 | 14.8896 | 15.8608 | 16.8889 | 17.9769 | 19.128 | 20.3457 | 21.6334 | 22.9951 | 24.4345 | 25.9559 | 27.5638 | 29.2627 | 31.0578 | 32.954 | 34.9572 | 37.073 | 39.3078 | 41.6681 | 44.1611 | 46.7941 | 49.5753
11.9117
10.1728
22.9175
|  |  |  | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 20 | 25 | 37
0
|  |  | 5 | -24.387 | -23.6718 | -22.9574 | -22.2439 | -21.5312 | -20.8194 | -20.1084 | -19.3983 | -18.689 | -17.9806 | -17.2731 | -16.5664 | -15.8605 | -15.1555 | -14.4513 | -13.7479 | -13.0454 | -12.3438 | -11.6429 | -10.9429 | -10.2438 | -9.5454 | -8.8479 | -8.1513 | -7.4554 | -6.7604
|  |  | 10 | -16.3925 | -15.6233 | -14.8548 | -14.0871 | -13.3202 | -12.5539 | -11.7884 | -11.0236 | -10.2596 | -9.4963 | -8.7337 | -7.9719 | -7.2107 | -6.4503 | -5.6906 | -4.9317 | -4.1735 | -3.416 | -2.6592 | -1.9031 | -1.1478 | -0.39314 | 0.36077 | 1.114 | 1.8664 | 2.6182
|  |  | 15 | -11.436 | -10.6324 | -9.8294 | -9.0271 | -8.2254 | -7.4244 | -6.6241 | -5.8243 | -5.0252 | -4.2268 | -3.429 | -2.6319 | -1.8354 | -1.0395 | -0.24425 | 0.55034 | 1.3443 | 2.1376 | 2.9303 | 3.7223 | 4.5137 | 5.3045 | 6.0947 | 6.8842 | 7.673 | 8.4613
|  |  | 20 | -7.7844 | -6.9549 | -6.126 | -5.2977 | -4.47 | -3.6429 | -2.8163 | -1.9903 | -1.1649 | -0.34001 | 0.48427 | 1.308 | 2.1311 | 2.9537 | 3.7757 | 4.5971 | 5.418 | 6.2382 | 7.058 | 7.8771 | 8.6957 | 9.5137 | 10.3312 | 11.1481 | 11.9644 | 12.7801
|  |  | 25 | -4.8709 | -4.0205 | -3.1706 | -2.3213 | -1.4725 | -0.62415 | 0.22365 | 1.0709 | 1.9177 | 2.7639 | 3.6097 | 4.4549 | 5.2996 | 6.1438 | 6.9875 | 7.8307 | 8.6734 | 9.5156 | 10.3572 | 11.1984 | 12.039 | 12.8791 | 13.7188 | 14.5579 | 15.3965 | 16.2346
|  |  | 30 | -2.4357 | -1.5676 | -0.70003 | 0.1671 | 1.0338 | 1.9 | 2.7657 | 3.631 | 4.4958 | 5.3602 | 6.2241 | 7.0876 | 7.9505 | 8.8131 | 9.6751 | 10.5367 | 11.3979 | 12.2586 | 13.1188 | 13.9786 | 14.838 | 15.6968 | 16.5552 | 17.4132 | 18.2707 | 19.1278
|  |  | 35 | -0.33718 | 0.54626 | 1.4293 | 2.3119 | 3.1941 | 4.0759 | 4.9572 | 5.8382 | 6.7188 | 7.5989 | 8.4786 | 9.3579 | 10.2368 | 11.1153 | 11.9934 | 12.8711 | 13.7483 | 14.6252 | 15.5016 | 16.3776 | 17.2532 | 18.1285 | 19.0033 | 19.8777 | 20.7516 | 21.6252
|  |  | 40 | 1.5107 | 2.4078 | 3.3045 | 4.2009 | 5.0969 | 5.9925 | 6.8878 | 7.7827 | 8.6772 | 9.5713 | 10.4651 | 11.3585 | 12.2515 | 13.1442 | 14.0365 | 14.9285 | 15.82 | 16.7113 | 17.6021 | 18.4926 | 19.3827 | 20.2724 | 21.1618 | 22.0508 | 22.9395 | 23.8277
|  |  | 45 | 3.1644 | 4.0738 | 4.9829 | 5.8917 | 6.8001 | 7.7082 | 8.616 | 9.5234 | 10.4305 | 11.3373 | 12.2438 | 13.1499 | 14.0557 | 14.9612 | 15.8663 | 16.7711 | 17.6756 | 18.5798 | 19.4837 | 20.3872 | 21.2904 | 22.1932 | 23.0958 | 23.998 | 24.8999 | 25.8014
|  |  | 50 | 4.663 | 5.5836 | 6.504 | 7.424 | 8.3438 | 9.2633 | 10.1825 | 11.1014 | 12.02 | 12.9383 | 13.8563 | 14.7741 | 15.6915 | 16.6087 | 17.5255 | 18.4421 | 19.3584 | 20.2744 | 21.1901 | 22.1056 | 23.0207 | 23.9356 | 24.8501 | 25.7644 | 26.6784 | 27.5921
|  |  | 55 | 6.0345 | 6.9655 | 7.8962 | 8.8267 | 9.7569 | 10.6869 | 11.6166 | 12.546 | 13.4752 | 14.4042 | 15.3329 | 16.2613 | 17.1895 | 18.1174 | 19.0451 | 19.9725 | 20.8997 | 21.8266 | 22.7533 | 23.6797 | 24.6058 | 25.5317 | 26.4574 | 27.3828 | 28.3079 | 29.2328
|  |  | 60 | 7.3001 | 8.2407 | 9.181 | 10.1212 | 11.0611 | 12.0008 | 12.9402 | 13.8795 | 14.8185 | 15.7573 | 16.6959 | 17.6343 | 18.5724 | 19.5103 | 20.448 | 21.3855 | 22.3228 | 23.2598 | 24.1966 | 25.1332 | 26.0696 | 27.0058 | 27.9417 | 28.8775 | 29.813 | 30.7482
|  |  | 65 | 8.4758 | 9.4254 | 10.3747 | 11.3239 | 12.2728 | 13.2216 | 14.1702 | 15.1186 | 16.0668 | 17.0148 | 17.9626 | 18.9103 | 19.8577 | 20.805 | 21.7521 | 22.6989 | 23.6456 | 24.5921 | 25.5385 | 26.4846 | 27.4305 | 28.3763 | 29.3219 | 30.2672 | 31.2124 | 32.1574
|  |  | 70 | 9.5744 | 10.5323 | 11.4901 | 12.4477 | 13.4052 | 14.3625 | 15.3196 | 16.2766 | 17.2334 | 18.1901 | 19.1466 | 20.103 | 21.0591 | 22.0152 | 22.9711 | 23.9268 | 24.8823 | 25.8377 | 26.793 | 27.7481 | 28.703 | 29.6577 | 30.6124 | 31.5668 | 32.5211 | 33.4752
|  |  | 75 | 10.6058 | 11.5717 | 12.5374 | 13.503 | 14.4685 | 15.4339 | 16.3991 | 17.3642 | 18.3291 | 19.2939 | 20.2586 | 21.2232 | 22.1877 | 23.152 | 24.1161 | 25.0802 | 26.0441 | 27.0079 | 27.9716 | 28.9351 | 29.8985 | 30.8618 | 31.8249 | 32.7879 | 33.7508 | 34.7136
|  |  | 80 | 11.5784 | 12.5518 | 13.5251 | 14.4982 | 15.4713 | 16.4443 | 17.4171 | 18.3899 | 19.3625 | 20.3351 | 21.3075 | 22.2799 | 23.2521 | 24.2243 | 25.1963 | 26.1683 | 27.1401 | 28.1119 | 29.0835 | 30.055 | 31.0265 | 31.9978 | 32.969 | 33.9402 | 34.9112 | 35.8821
|  |  | 85 | 12.4989 | 13.4794 | 14.4598 | 15.4402 | 16.4205 | 17.4007 | 18.3808 | 19.3608 | 20.3408 | 21.3207 | 22.3005 | 23.2803 | 24.26 | 25.2396 | 26.2191 | 27.1985 | 28.1779 | 29.1572 | 30.1364 | 31.1156 | 32.0946 | 33.0736 | 34.0526 | 35.0314 | 36.0102 | 36.9889
|  |  | 90 | 13.373 | 14.3603 | 15.3475 | 16.3347 | 17.3218 | 18.3089 | 19.296 | 20.283 | 21.2699 | 22.2568 | 23.2437 | 24.2305 | 25.2172 | 26.2039 | 27.1906 | 28.1772 | 29.1637 | 30.1502 | 31.1367 | 32.1231 | 33.1095 | 34.0958 | 35.082 | 36.0682 | 37.0544 | 38.0405
|  |  | 95 | 14.2053 | 15.1991 | 16.1928 | 17.1866 | 18.1803 | 19.174 | 20.1676 | 21.1613 | 22.1549 | 23.1485 | 24.142 | 25.1356 | 26.1291 | 27.1226 | 28.1161 | 29.1095 | 30.1029 | 31.0963 | 32.0897 | 33.083 | 34.0764 | 35.0697 | 36.0629 | 37.0562 | 38.0494 | 39.0426
|  |  | 100 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
|  |  | 100: 80 | 16.4443
|  |  | 100: 50 |  | 13.8563
|  |  | 100: 55 |  |  | 26.4574
|  |  |  | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 20 | 25 | 37
|  |  | 0 | 15.15 | 16.16 | 17.17 | 18.18 | 19.19 | 20.2 | 21.21 | 22.22 | 23.23 | 24.24 | 25.25 | 26.26 | 27.27 | 28.28 | 29.29 | 30.3 | 31.31 | 32.32 | 33.33 | 34.34 | 35.35 | 36.36 | 37.37 | 38.38 | 39.39 | 40.4
|  |  | 5 | 16.5141 | 17.6171 | 18.7259 | 19.8406 | 20.9616 | 22.0893 | 23.2241 | 24.3662 | 25.5162 | 26.6744 | 27.8413 | 29.0173 | 30.2031 | 31.399 | 32.6056 | 33.8236 | 35.0536 | 36.2961 | 37.552 | 38.822 | 40.1067 | 41.4072 | 42.7242 | 44.0587 | 45.4117 | 46.7843
|  |  | 10 | 17.8782 | 19.0743 | 20.2817 | 21.5012 | 22.7333 | 23.9787 | 25.2381 | 26.5124 | 27.8024 | 29.1088 | 30.4326 | 31.7747 | 33.1361 | 34.5179 | 35.9212 | 37.3472 | 38.7971 | 40.2723 | 41.774 | 43.3039 | 44.8635 | 46.4544 | 48.0784 | 49.7374 | 51.4335 | 53.1686
|  |  | 15 | 19.2423 | 20.5314 | 21.8376 | 23.1618 | 24.5049 | 25.868 | 27.2522 | 28.6587 | 30.0885 | 31.5432 | 33.0238 | 34.532 | 36.0692 | 37.6369 | 39.2369 | 40.8708 | 42.5407 | 44.2484 | 45.9961 | 47.7859 | 49.6202 | 51.5016 | 53.4326 | 55.4161 | 57.4552 | 59.5529
|  |  | 20 | 20.6064 | 21.9886 | 23.3935 | 24.8224 | 26.2765 | 27.7574 | 29.2663 | 30.8049 | 32.3747 | 33.9775 | 35.6151 | 37.2893 | 39.0022 | 40.7559 | 42.5525 | 44.3945 | 46.2843 | 48.2245 | 50.2181 | 52.2678 | 54.377 | 56.5488 | 58.7868 | 61.0949 | 63.4769 | 65.9372
|  |  | 25 | 21.9705 | 23.4457 | 24.9494 | 26.483 | 28.0482 | 29.6467 | 31.2804 | 32.9511 | 34.6609 | 36.4119 | 38.2064 | 40.0467 | 41.9353 | 43.8748 | 45.8681 | 47.9181 | 50.0278 | 52.2007 | 54.4401 | 56.7498 | 59.1337 | 61.596 | 64.141 | 66.7736 | 69.4986 | 72.3215
|  |  | 30 | 23.3345 | 24.9029 | 26.5052 | 28.1436 | 29.8198 | 31.536 | 33.2944 | 35.0973 | 36.9471 | 38.8463 | 40.7977 | 42.804 | 44.8683 | 46.9938 | 49.1837 | 51.4417 | 53.7714 | 56.1768 | 58.6621 | 61.2318 | 63.8905 | 66.6432 | 69.4952 | 72.4523 | 75.5204 | 78.7058
|  |  | 35 | 24.6986 | 26.36 | 28.0611 | 29.8042 | 31.5914 | 33.4254 | 35.3085 | 37.2435 | 39.2333 | 41.2807 | 43.3889 | 45.5613 | 47.8014 | 50.1128 | 52.4994 | 54.9653 | 57.515 | 60.153 | 62.8842 | 65.7137 | 68.6472 | 71.6904 | 74.8494 | 78.131 | 81.5421 | 85.0902
|  |  | 40 | 26.0627 | 27.8171 | 29.617 | 31.4648 | 33.3631 | 35.3147 | 37.3226 | 39.3898 | 41.5194 | 43.7151 | 45.9802 | 48.3187 | 50.7344 | 53.2317 | 55.815 | 58.4889 | 61.2585 | 64.1291 | 67.1062 | 70.1957 | 73.4039 | 76.7376 | 80.2036 | 83.8097 | 87.5638 | 91.4745
|  |  | 45 | 27.4268 | 29.2743 | 31.1729 | 33.1254 | 35.1347 | 37.2041 | 39.3367 | 41.536 | 43.8056 | 46.1495 | 48.5715 | 51.076 | 53.6675 | 56.3507 | 59.1306 | 62.0125 | 65.0021 | 68.1052 | 71.3282 | 74.6777 | 78.1607 | 81.7847 | 85.5578 | 89.4884 | 93.5855 | 97.8588
|  |  | 50 | 28.7909 | 30.7314 | 32.7287 | 34.786 | 36.9064 | 39.0934 | 41.3507 | 43.6822 | 46.0918 | 48.5838 | 51.1628 | 53.8333 | 56.6005 | 59.4697 | 62.4462 | 65.5362 | 68.7457 | 72.0814 | 75.5502 | 79.1596 | 82.9174 | 86.8319 | 90.912 | 95.1671 | 99.6073 | 104.2431
|  |  | 55 | 30.155 | 32.1886 | 34.2846 | 36.4465 | 38.678 | 40.9827 | 43.3648 | 45.8284 | 48.378 | 51.0182 | 53.7541 | 56.5907 | 59.5336 | 62.5886 | 65.7618 | 69.0598 | 72.4892 | 76.0575 | 79.7722 | 83.6416 | 87.6742 | 91.8791 | 96.2663 | 100.8459 | 105.629 | 110.6274
|  |  | 60 | 31.5191 | 33.6457 | 35.8405 | 38.1071 | 40.4496 | 42.8721 | 45.3789 | 47.9746 | 50.6642 | 53.4526 | 56.3453 | 59.348 | 62.4667 | 65.7076 | 69.0775 | 72.5834 | 76.2328 | 80.0336 | 83.9943 | 88.1235 | 92.4309 | 96.9263 | 101.6205 | 106.5246 | 111.6507 | 117.0117
|  |  | 65 | 32.8832 | 35.1029 | 37.3964 | 39.7677 | 42.2213 | 44.7614 | 47.393 | 50.1208 | 52.9503 | 55.887 | 58.9366 | 62.1053 | 65.3997 | 68.8265 | 72.3931 | 76.107 | 79.9764 | 84.0098 | 88.2163 | 92.6055 | 97.1876 | 101.9735 | 106.9747 | 112.2033 | 117.6724 | 123.396
|  |  | 70 | 34.2473 | 36.56 | 38.9522 | 41.4283 | 43.9929 | 46.6508 | 49.407 | 52.2671 | 55.2365 | 58.3214 | 61.5279 | 64.8627 | 68.3328 | 71.9455 | 75.7087 | 79.6306 | 83.72 | 87.9859 | 92.4383 | 97.0875 | 101.9444 | 107.0207 | 112.3289 | 117.882 | 123.6942 | 129.7803
|  |  | 75 | 35.6114 | 38.0172 | 40.5081 | 43.0889 | 45.7645 | 48.5401 | 51.4211 | 54.4133 | 57.5227 | 60.7558 | 64.1192 | 67.62 | 71.2658 | 75.0645 | 79.0243 | 83.1542 | 87.4635 | 91.9621 | 96.6603 | 101.5694 | 106.7011 | 112.0679 | 117.6831 | 123.5607 | 129.7159 | 136.1646
|  |  | 80 | 36.9755 | 39.4743 | 42.064 | 44.7495 | 47.5362 | 50.4294 | 53.4352 | 56.5595 | 59.8089 | 63.1901 | 66.7104 | 70.3774 | 74.1989 | 78.1834 | 82.34 | 86.6779 | 91.2071 | 95.9382 | 100.8824 | 106.0514 | 111.4579 | 117.1151 | 123.0373 | 129.2394 | 135.7376 | 142.5489
|  |  | 85 | 38.3395 | 40.9314 | 43.6199 | 46.4101 | 49.3078 | 52.3188 | 55.4492 | 58.7057 | 62.0951 | 65.6245 | 69.3017 | 73.1347 | 77.1319 | 81.3024 | 85.6556 | 90.2015 | 94.9507 | 99.9143 | 105.1044 | 110.5334 | 116.2146 | 122.1623 | 128.3915 | 134.9182 | 141.7594 | 148.9332
|  |  | 90 | 39.7036 | 42.3886 | 45.1757 | 48.0707 | 51.0794 | 54.2081 | 57.4633 | 60.8519 | 64.3812 | 68.0589 | 71.893 | 75.892 | 80.065 | 84.4214 | 88.9712 | 93.7251 | 98.6942 | 103.8905 | 109.3264 | 115.0153 | 120.9714 | 127.2095 | 133.7457 | 140.5969 | 147.7811 | 155.3175
|  |  | 95 | 41.0677 | 43.8457 | 46.7316 | 49.7313 | 52.8511 | 56.0975 | 59.4774 | 62.9982 | 66.6674 | 70.4933 | 74.4843 | 78.6494 | 82.998 | 87.5403 | 92.2868 | 97.2487 | 102.4378 | 107.8666 | 113.5484 | 119.4973 | 125.7281 | 132.2567 | 139.0999 | 146.2756 | 153.8028 | 161.7019
|  |  | 100 | 42.4318 | 45.3029 | 48.2875 | 51.3919 | 54.6227 | 57.9868 | 61.4915 | 65.1444 | 68.9536 | 72.9277 | 77.0755 | 81.4067 | 85.9311 | 90.6593 | 95.6025 | 100.7723 | 106.1814 | 111.8427 | 117.7704 | 123.9792 | 130.4848 | 137.3039 | 144.4541 | 151.9543 | 159.8245 | 168.0862
|  |  | 0: 80 | 50.4294
|  |  | 0: 50 |  | 51.1628
|  |  | 0: 55 |  |  | 96.2663
Max water saturation pressure (Pws) | 23.3789 | 31.6745 | 0: 62.7854; 15 15.15: hPa
Water saturation pressure (Pws) | 18.7032 | 15.8373 | 0: 34.532; 15 15.15: hPa
X | 14.8896 | 20.3457 | 0: 41.6681; 15 15.15: g/kg